## Sheet1
Item Wise BoQ
BoQ_Ver3.1 |  | Item Wise | INR and Other Currency
Tender Inviting Authority: Purchase cum Stores Officer, NIPGR, New Delhi
Name of Work: Supply, Installation, Testing & Commissioning of Automatic Fire Suppression System for Server Racks in NIPGR Campus, New Delhi.
Contract No: NIPGR/Engg./6/_____/2022-23
Name of the Bidder/ Bidding Firm / Company :
PRICE SCHEDULE (This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevant columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only )
(This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevant columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only )
NUMBER # | TEXT # | TEXT # | NUMBER # | TEXT # | NUMBER # | NUMBER | NUMBER # | NUMBER # | NUMBER #
Sl. No. | Particulars | Item Description | Quantity | Units | UNIT RATE In Figures To be entered by the Bidder in Rs. P | GST in Rs. P (Col. 5 x % of GST) | Total Unit Rate with GST (Col. 5+6) | TOTAL AMOUNT Without Taxes in Rs. P (Col. 3 x 5) | TOTAL AMOUNT With Taxes in Rs. P (Col. 3 x 7)
1 |  | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9
1 | Supply of 2 Kg Automatic Direct Low Pressure Fire Suppression. Extinguisher and Valve | Extinguishant :- Clean Agent HFC 227 with Zero Ozone Depletion Potential | 9 | Each | 0 | 0 | 0 | 0 | 0
CAN : Stored Pressure Type, fitted with Pressure Gauge,Weight 2 kg. Discharge time variable, is dependent on tube length, distance of pipe rupture from cylinder traveling along tube and pipe rupture's size (approx 35-60 seconds). Applicable on class A, B, C and electrically started fires.
Can Construction : Deep drawn and Co2 Mig welded, Internal Coating of Can : Epoxy Powder Coating, External Coating of Can Epoxy Polyester Powder Coating, Sheet metal thickness 1.60MM, Hydraulic Pressure Tested to 35 bars,operating pressure 15 bar. Helium Leak Detection Tested. Confirms to EN standards. Manufactured at ISO 9001 certified factory.
Valve : Direct Low Pressure with Integrated ball valve to minimize leakages, Integrated position monitoring of valve for open / close position of valve using potential free switch contact. Special key for locking valve position to avoid accidental closure, Operating pressure 15 bar tested upto 35 bars, 2 Tube connections
2 | Pressure Switch | Supply of Pressure Switch to monitor Pressure in the tube, switch point 11 Bars. | 9 | Each | 0 | 0 | 0 | 0 | 0
3 | Heat Sensor Tube for Automatic Fire Suppression System | Supply of Heat Sensor tube for automatic fire suppression system made by special modified Polyamide (PA), Color Black, High grade HR quality, UV Stabilized, Inner diameter 4mm, Outer Diameter 6 MM, Melting Point approx. 220 degrees Celsius when heating up with 10 K/minute, Steady load tested upto max. 80° C. The lowest operating temperature is stipulated at minus 40°C. Service Pressure 15 Bar, Burst Pressure at 20 Deg C approx 120 Bars, Release Temperature : Rapid heat increase in temperature at 15 bars pressure approx 150 Deg to 180 Deg C (Without Flame) | 140 | Rmtr. | 0 | 0 | 0 | 0 | 0
4 | End of Line Adapter | Supply of End of Line adapter for Pressure gauge fitting for Automatic fire suppression tube used for fitting at the end of the tube for pressurizing and re pressurizing the tube. Fitting made by brass (plated / unplated), Stainless steel, Elastomeric Sealings, Copper Nickle plated, Temperature range TS -20 Deg C till + 60 Deg C, Maximum working pressure 25 Bars | 9 | Each | 0 | 0 | 0 | 0 | 0
5 | Response Indication Panel | S.I.T.C. of Control Panel with monitoring LED's for AC Power On, System On, Discharged, Valve Closed, Valve Open, Pressure Healthy, Strobe Lights, 6 Volts SMF Battery Backup, 3 Inputs for Discharge, Valve Status, Pressure Switch, 3 Outputs via Potential Free Relay Contact NO/NC/COM 9. 50 db Piezo Buzzer Output along with 24V DC Hooters. | 9 | Each | 0 | 0 | 0 | 0 | 0
6 | Installation & Commissioning Charges | Installation, testing & Commissioning includes complete setup of the system, Installation of Cylinders, response panel on specially designed brackets, Laying of sensor tubes using tube attachments, T-connections and Cable ties, fixing end of line plugs and end of line adapters, pressurizing tube @ 15 Bars using Nitrogen pressurizing agent and making electrical connections & power points for the panels. | 9 | Each | 0 | 0 | 0 | 0 | 0
Total in figures |  | 8: 0; 9: 0
Quoted Rate in Words
|  | Purchase cum Stores Officer |  |  |  | Seal & Signature of Contractor