## Sheet1
BoQ_Ver3.1 | Item Wise |  | INR and Other Currency
Tender Inviting Authority: Purchase cum Stores Officer, NIPGR, New Delhi
Name of Work: Repairing of chillers installed at Plant Growth Facility at NIPGR Campus, New Delhi.
Contract No: NIPGR/Engg./5/1/2022-23
Name of the Bidder/Bidding Firm / Company:
PRICE SCHEDULE (This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevant columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only )
(This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevant columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only )
NUMBER # | TEXT # | NUMBER # | TEXT # | NUMBER # | NUMBER | NUMBER # | NUMBER # | NUMBER #
Sl. No. | Item Description | Quantity | Units | UNIT RATE In Figures To be entered by the Bidder in Rs. P | GST in Rs. P (Col. 5 x % of GST) | Total Unit Rate with GST (Col. 5+6) | TOTAL AMOUNT Without Taxes in Rs. P (Col. 3 x 5) | TOTAL AMOUNT With Taxes in Rs. P (Col. 3 x 7)
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9
1 | Supply & installation of air cooled chiller cooling coil made of copper tube, aluminium Fins, 27gauge & 11-13 fins per inch, . Chilled water coils shall have 12.5mm to 16mm dia tubes of wall thickness not less than 27G (0.41mm thick with aluminium fins firmly bonded to copper tubes assembled in zinc coated steel frame. Face and surface area shall be such as to ensure rated capacity from each unit and such that air velocity across each coil shall not exceed 500 FPM. the coil shall pitched in the unit casing for proper drainage. Each coil shall be factory tested at 30 kg/cm2 pressure Tubes shall be hydraullically / mechanically expanded for minimum thermal contact resistance with fins. Fin spacing shall be 11 to 13 fins per inch. The scope of work also includes removal of damaged existing cooling coil from chiller,replacement of defective compressors with new, cutting-welding, insulation, oil filter etc. and complete as per site requirement. If any variation in specification agency is requested to match the same with existing installation and same shal be considered. The cooling coil should be certified by AHRI or ASHRAE. The capacity of each chiller shall be 48 TR. Makes: - ZECO / EDGETECH/ BLUESTAR / VOLTAS | 3 | nos | 0 | 0 | 0 | 0 | 0
2 | Gas charging in the chiller coils complete in order to make system functional | 150 | Kg. | 0 | 0 | 0 | 0 | 0
3 | Testing and commissioning of the airconditioning system to make system functional | 3 | nos | 0 | 0 | 0 | 0 | 0
Scope of work for all three chillers includes Dismantling and removal of old coil, Replacement of defective compressors, fixing of new coil with fittings and necessary brazing, supply and Charging of Nitrogen gas with sufficient pressure and pressure testing of the system. Vaccumisation of the entire system. Charging of refrigerant gas, commissioning of the system and trials
Total in figures | [6 empty] | 0 | 0
Quoted Rate in Words
| Purchase cum Stores Officer |  |  |  |  | Seal & Signature of Contractor