## pricebid
Item Wise BoQ
BoQ_Ver3.1 | Item Wise |  | INR and Other Currency
Tender Inviting Authority: Consultant Engineer, NIPGR, New Delhi
Name of Work: Establishment of Infrastructure for HRD Conference Room regarding supply, installation, testing & commissioning of HVAC system in Lab 007 at NIPGR Campus, New Delhi.
Contract No: NIPGR/Engg./5/19/2024-25
Name of the Bidder/ Bidding Firm / Company :
PRICE SCHEDULE (This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevant columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only )
(This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevant columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only )
NUMBER # | TEXT # | NUMBER # | TEXT # | NUMBER # | NUMBER | NUMBER # | NUMBER # | NUMBER #
Sl. No. | Item Description | Quantity | Units | UNIT RATE In Figures To be entered by the Bidder in Rs. P | GST in Rs. P (Col. 5 x % of GST) | Total Unit Rate with GST (Col. 5+6) | TOTAL AMOUNT Without Taxes in Rs. P (Col. 3 x 5) | TOTAL AMOUNT With Taxes in Rs. P (Col. 3 x 7)
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9
1 | SUB WORK 'A'-MACHINERY
Variable Refrigerant Volume / Flow system - Daikin / LG / Mitsubishi Heavy
Supplying, Installation, testing and commissioning of following nominal capacity Air Cooled 100% Inverter based Variable refrigerant flow / volume Scroll modular type air-conditioning system. The units shall be suitable for operation on 3 phase Supply. The units shall have cooling and heating type, low noise condenser fans, auto address setting, auto check function for connection error and complete with indoor and outdoor units with individual controller and with fittings etc. as per quantity given below including full charging of R-410A refrigerant gas i/c powder coating of all metalic encloser. The fan static pressure of the outdoor unit shall be more then 75 Pa to avoid hot air recirculation. Condenser shall have with hydrophilic coating and corrosion resistance Ocean Black Fin coating. The compressor shall have inverter technology i.e outdoor units shall have all inverter compressor. The manufacture of ODU and compresser shall be same i.e make of compressor shall be identical of the ODU make. The scope includes dismantling & remaking of false ceiling, all civil workis , foundation works in the above item
1.1 | Supply Instalaltion, testing & commissioning of Outdoor Unit
COP of system 3.7 at 100% load & 7.50 at 50% at AHRI condition.The unit shall also have feature to automatically modulate the evaporative temperature between 6 deg C to 10 deg C with respect to load for better comfort and energy efficiency.
Operating range Outdoor Unit shall be capable of maintaining continuous compressor operation under all of the following operating ambient air conditions. a) Operating ambient air conditions - Cooling: -5°C DB to 53°C DB
No derating of cooling capacity at 39 deg C ambient
Inverter PCB cooling: Cooling of the inverter PCB shall be conducted by way of high pressure, sub-cooled liquid refrigerant via heat exchanger attached to rear side of inverter PCB. The full capacity flow of refrigerant shall pass through the heat exchangers to maximize the cooling effect of the PCBs and to aid in the evaporation process and capacity of the outdoor coil during the heating mode. The recovered heat of the PCBs must be used to enhance the overall heating process, other uses or dissipation of heat to ambient shall not be permitted.
a | 10 HP capacity | 3 | each | 0 | 0 | 0 | 0 | 0
b | 6 HP capacity | 1 | each | 0 | 0 | 0 | 0 | 0
2 | INDOOR UNIT-DUCTABLE TYPE
Supply, installation, testing and commissioning of following minimum capacity and external static pressure VRF/VRV ceiling mounted ductable type Indoor unit equipped with washable synthetic media pre-filter, fan section with low noise fan/dynamically balanced blower, multispeed motor, coil section with DX copper coil, electronic expansion valve, cordless remote control, outer cabinet, vibration isolators, drain pan, other necessary supports etc., suitable for operation on single phase AC supply 230 V ± 10%, 50 Hz complete as required. The unit shall have automatic force shut down provision in case of fire on receiveing signal from BMS System. The cooling capacity of indoor unit will be at air inlet conditions of 27 Degree C DB and 19 Degree C WB temperature.
Mid Static Ductable units (minimum 45 pascal external static pressure)
2.1 | 2.0 TR | 1 | each | 0 | 0 | 0 | 0 | 0
| High Static Ductable units (minimum 110 pascal external static pressure) |  |  | 0 | 0 | 0 | 0 | 0
2.2 | 8.0 TR | 2 | each | 0 | 0 | 0 | 0 | 0
2.3 | 4.5 TR | 1 | each | 0 | 0 | 0 | 0 | 0
Note:- Backdraft dampers shall be provided at the outlet of each 8.0 TR ductable unit.
3 | INDOOR UNIT-HIWALL TYPE
Supply, installation, testing and commissioning of Wall mounted Type Indoor Units each complete with coil, filter, etc. Air conditioners with evaporating unit comprising of cooling coil, blower with motor suitable for operation on 230 volt, 1 phase, 50 Hz, AC supply and as per specifications. The rate shall include cost of cordless Remote controller, Top Plugs, complete length of required size drain pipes and all other accessories required for full-fledged operation of system. Nothing extra shall be paid in this account.
3.1 | 1.6 TR | 3 | each | 0 | 0 | 0 | 0 | 0
4 | Supply, Installation, Testing and commissioning of Imported fittings (Ref Net) Y-joints etc. | 3 | Nos. | 0 | 0 | 0 | 0 | 0
5 | Supplying, installation, testing and commissioning of Central Remote Controller for integrating and effecient control of Indoor and Outdoor Units from Station Controller room. Rate shall include all required and asssociated accessories for complete functionality of the equipment as per technical specification. The equipment shall have inbulit compatability for integration with BMS susytem through RS485 communication port with MODBUS protocol. | 1 | Set | 0 | 0 | 0 | 0 | 0
| TOTAL SUB WORK 'A' |  |  | 0 | 0 | 0 | 0 | 0
SUB WORK 'B'- AIR DISTRIBUTION
1 | DUCTING, GRILLS, DIFFUSER AND INSULATION
Supply, installation, balancing and commissioning of factory fabricated GSS sheet metal rectangular/round ducting complete with neoprene rubber gaskets, elbows, splitter dampers, vanes, hangers, supports etc. as per approved drawings and specifications of following sheet thickness complete as required.
1.1 | Thickness 0.63 mm sheet (24G) | 50 | Sqm | 0 | 0 | 0 | 0 | 0
1.2 | Thickness 0.80 mm sheet (22G) | 10 | Sqm | 0 | 0 | 0 | 0 | 0
Make: Ductofab/ADS/Zeco
Make for GSS Sheet: TATA/Bhushan/SAIL
2 | Duct Insulation
Supplying , installation, testing & commissioning of external thermal insulation on ducts with Duly laminated aluminum foil of mat finish Closed Cell Nitrile Rubber (class “O”) insulation after applying of suitable adhesive for nitrile rubber. The joints shall be sealed with 50 mm wide and 3 mm thick self adhesive nitrile rubber tape insulation complete as per tender specification
2.1 | 19 mm thick Closed Cell Nitrile rubber insulation with Factory Laminated Aluminium Foil for Supply Air Duct | 50 | Sqm | 0 | 0 | 0 | 0 | 0
Makes: Armacell/A Flex/ K Flex
3 | Acoustic Lining
Supply, Installation, Testing and Commissioning of Acoustic lining inside ducts using open cell elastomeric insulation with antimicrobial protection having 140-160 kg/cum density & as per specifications
3.1 | 15mm thick armasound | 10 | Sqm | 0 | 0 | 0 | 0 | 0
Makes: Armacell/A Flex/ K Flex
4 | Supply Air Diffuser
| Supplying, fixing testing commissioning of supply air diffusers of powder coated aluminium with aluminium volume control dampers with anti smudge ring & removable core | 1 | Sqm | 0 | 0 | 0 | 0 | 0
Make: Mapro/ADS/System Air / Caryaire
5 | Return Air Diffuser
| Supplying, fixing testing commissioning of supply air diffusers of powder coated aluminium with aluminium volume control dampers with anti smudge ring & removable core | 1 | Sqm | 0 | 0 | 0 | 0 | 0
Make: Mapro/ADS/System Air / Caryaire
| TOTAL SUB WORK 'B' |  |  | 0 | 0 | 0 | 0 | 0
SUB WORK 'C'- PLUMBING
1 | REFRIGERANT PIPING
Supply, Installation, testing and commissioning including vaccumiazation and Nitrogen testing of following nominal sizes of soft/hard drawn copper refrigerant piping for VRV/VRF system, complete with fittings, with suitable adjustable ring type hanger supports, jointing/brazing including accessories, insulated with XPLE Class-O tubular insulation/with Class-O closed cell elastometric nitrile rubber tubular sleeves sections of specified thickness as given below for Suction and Liquid lines, all accessories as per specifications etc. as required :
1.1 | 6.4 mm dia (OD) (Soft drawn) with tube thickness 1.2 mm with 13 mm thick insulation | 10 | RM | 0 | 0 | 0 | 0 | 0
1.2 | 9.5 mm dia (OD) (Soft drawn) with tube thickness 1.2 mm with 13 mm thick insulation | 25 | RM | 0 | 0 | 0 | 0 | 0
1.3 | 12.7 mm dia (OD) (Soft drawn) with tube thickness 1.2 mm with 13 mm thick insulation | 12 | RM | 0 | 0 | 0 | 0 | 0
1.4 | 15.86 mm dia (OD) (Soft drawn) with tube thickness 1.2 mm with 13 mm thick insulation | 5 | RM | 0 | 0 | 0 | 0 | 0
1.5 | 19 mm dia (OD) (Hard drawn) with tube thickness 1.2 mm with 13 mm thick insulation | 10 | RM | 0 | 0 | 0 | 0 | 0
1.6 | 22.2 mm dia (OD) (Hard drawn) with tube thickness 1.2 mm with 13 mm thick insulation | 10 | RM | 0 | 0 | 0 | 0 | 0
1.7 | 28.58 mm dia (OD) (Hard drawn) with tube thickness 1.2 mm with 19 mm thick insulation | 10 | RM | 0 | 0 | 0 | 0 | 0
NOTE:- (1) The Copper Piping & Piping Circuit should be with Minimum Number of joints, which shall be attained by : (i) Using One End Expanded Tubes (ii) Bending the tubes instead of using elbow joints wherever 90 degree bending is required. (2) Piping should be routed at site in such a manner, that brazed joints in the refrigeration piping are kept to a minimum. (3) The makes of tube fittings shall be same as that of tubes. (4) The thickness of fittings used shall be same as that of the pipe.
Makes of Copper Pipe: Mandev/Rajco/Maxflow
Makes of XLPE Insulation: Trocellen/CANI/Armacell / K Flex
2 | PVC Drain Piping
Supply, Installation, testing and commissioning of PVC piping complete with fittings, supports accessories in surface/recess as per specifications & site requirments including with duly insulated with 6 mm thick sleeve of nitrle rubber having K value 0.033 W/MK at 10 deg. C mean temp. and minimum density of 25 Kg/Cum. Insulation on drain pipe
2.1 | 25 mm Dia | 35 | m | 0 | 0 | 0 | 0 | 0
2.2 | 32 mm dia | 5 | m | 0 | 0 | 0 | 0 | 0
Makes: AKG/Supreme/Astral
| TOTAL SUB WORK 'C' |  |  | 0 | 0 | 0 | 0 | 0
D | SUB WORK 'D'- ELECTRIC WORKS
1 | Weather Proof isolators for Outdoor Units
Supplying, installation testing and commissioning of 415 volt three phase and neutral swith outlets TPN MCCB/MCB iasolator in weather proof IP 65 enclosure. The quantities of isolators is as follows.
1.1 | 40 amps TPN MCB in weather proof enclosure for 1 Nos. 10 HP VRV outdoor units. | 3 | each | 0 | 0 | 0 | 0 | 0
1.2 | 32 amps TPN MCB in weather proof enclosure for 1 Nos. 6 HP VRV outdoor units. | 1 | each | 0 | 0 | 0 | 0 | 0
Makes: LEGRAND/ABB/ SEIMENS / L & T
2 | Power Cabling
Supply and laying of the following 1100 volt grade armoured XLPE insulated and PVC sheathed aluminium conductor cable in trench / cable tray /clamped to wall with suitable clamps saddles & fixing bolts/including testing & commissioning complete as required. The costs shall include crimping tinned heavy duty alluminium lugs, compression glands requisite materials for all cables and to provide with 1D gap & shall be properly clamped with cable clamps & ties. Identification tags shall be provided for all cables including cable end termination.
2.1 | 4 core 10 Sq mm | 10 | RM | 0 | 0 | 0 | 0 | 0
2.2 | 4 core 6 Sq mm | 10 | RM | 0 | 0 | 0 | 0 | 0
Makes: POLYCAB / FINOLEX / KEI
3 | CONTROL CABLING
Supply, laying, testing and commissioning of PVC insulated and PVC sheathed, unarmoured, Copper Conductor of 1.1 KV grade on existing cable trays as per Standard specification including end termination as required.
3.1 | 2C x 1.0 Sq mm | 20 | RM | 0 | 0 | 0 | 0 | 0
3.2 | 3C x 2.5 Sq mm | 30 | RM | 0 | 0 | 0 | 0 | 0
Makes: POLYCAB / FINOLEX / KEI
4 | Electrical Cable Tray
Supply and installation of following size of perforated painted with powder coating G.I. cable trays with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with G.I. suspenders including bolts & nuts, painting suspenders etc as required.
4.1 | 100 mm width X 50 mm depth X 1.6 mm thickness | 10 | RM | 0 | 0 | 0 | 0 | 0
4.2 | 250 mm width X 50 mm depth X 1.6 mm thickness | 40 | RM | 0 | 0 | 0 | 0 | 0
5 | Earthing |  |  |  | 0
Makes: RALBO/ MEM / SLOTCO
| Providing and fixing 6 SWG dia G.I. wire on surface or in recess for loop earthing as required. | 80 | RM | 0 | 0 | 0 | 0 | 0
| TOTAL SUB WORK 'D' |  |  | 0 | 0 | 0 | 0 | 0
1 | SUB WORK 'A'-MACHINERY |  |  | 0 | 0 | 0 | 0 | 0
2 | SUB WORK 'B'- AIR DISTRIBUTION |  |  | 0 | 0 | 0 | 0 | 0
3 | SUB WORK 'C'- PLUMBING |  |  | 0 | 0 | 0 | 0 | 0
4 | SUB WORK 'D'- ELECTRIC WORKS |  |  | 0 | 0 | 0 | 0 | 0
Total in figures |  |  |  | 0 | 0 | 0 | 0 | 0
Quoted Rate in Words
| Consultant Engineer |  |  |  | Seal & Signature of Contractor