## pricebid
Item Wise BoQ
BoQ_Ver3.1 | Item Wise |  | INR and Other Currency
Tender Inviting Authority: Director, NIPGR, New Delhi
Name of Work: Supply, Installation, Testing & Commissioning of ductable Air conditioner for Archives Room at NIPGR Campus, New Delhi.
Contract No: NIPGR/Engg./5/3/2024-25
Name of the Bidder/ Bidding Firm / Company :
PRICE SCHEDULE (This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevant columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only )
(This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevant columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only )
NUMBER # | TEXT # | NUMBER # | TEXT # | NUMBER # | NUMBER | NUMBER # | NUMBER # | NUMBER #
Sl. No. | Item Description | Quantity | Units | UNIT RATE In Figures To be entered by the Bidder in Rs. P | GST in Rs. P (Col. 5 x % of GST) | Total Unit Rate with GST (Col. 5+6) | TOTAL AMOUNT Without Taxes in Rs. P (Col. 3 x 5) | TOTAL AMOUNT With Taxes in Rs. P (Col. 3 x 7)
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9
1 | SUB WORK 'A'-MACHINERY
Make Daikin / LG / Carrier/ Voltas/ Equivalent
UNIT-DUCTABLE TYPE
Supply Installation Testing and Commissioning of R410a Refrigerant type, 8.5 TR Ductable split unit with Indoor and outdoor units with inverter technology Compressors, thermostat and all standard accessories etc. Indoor unit comprising of Ductable split air conditioners with indoor unit comprising of pre-filter, low noise Copper Coil with fan section, etc. complete. The fan for outdoor unit shall be selected for low noise and the motor etc. shall be housed in a powder coated casing. Indoor unit shall be acoustically treated and shall be controlled with wireless remote / wireless microprocessor intelligent system with single phase prevention, reverse phase protection etc. Outdoor units shall be provided with suitable size angle iron stand on RCC civil foundations etc,. duly painted and as directed. (single circuit machine shall be supplied). The Machine shall be supplied and installed with Fire dampers with interlocking with each other considering two working and one standby at a time. The cost of all the same must be quoted in the said item.
High Static Ductable units (minimum 110 pascal external static pressure)
2.2 | 8.5 TR | 3 | each | 0 | 0 | 0 | 0 | 0
Note:- Backdraft dampers shall be provided at the outlet of each 8.0 TR ductable unit.
| TOTAL SUB WORK 'A' |  |  | 0 | 0 | 0 | 0 | 0
SUB WORK 'B'- AIR DISTRIBUTION
1 | DUCTING, GRILLS, DIFFUSER AND INSULATION
Supply, installation, balancing and commissioning of factory fabricated GSS sheet metal rectangular/round ducting complete with neoprene rubber gaskets, elbows, splitter dampers, vanes, hangers, supports etc. as per approved drawings and specifications of following sheet thickness complete as required.
1.1 | Thickness 0.63 mm sheet (24G) | 50 | Sqm | 0 | 0 | 0 | 0 | 0
1.2 | Thickness 0.80 mm sheet (22G) | 10 | Sqm | 0 | 0 | 0 | 0 | 0
Make: Ductofab/ADS/Zeco/ Equivalent
Make for GSS Sheet: TATA/Bhushan/SAIL/Equivalent
2 | Duct Insulation
Supplying , installation, testing & commissioning of external thermal insulation on ducts with Duly laminated aluminum foil of mat finish Closed Cell Nitrile Rubber (class “O”) insulation after applying of suitable adhesive for nitrile rubber. The joints shall be sealed with 50 mm wide and 3 mm thick self adhesive nitrile rubber tape insulation complete as per tender specification
2.1 | 19 mm thick Closed Cell Nitrile rubber insulation with Factory Laminated Aluminium Foil for Supply Air Duct | 10 | Sqm | 0 | 0 | 0 | 0 | 0
Makes: Armacell/A Flex/ K Flex/Equivalent
3 | Acoustic Lining
Supply, Installation, Testing and Commissioning of Acoustic lining inside ducts using open cell elastomeric insulation with antimicrobial protection having 140-160 kg/cum density & as per specifications
3.1 | 15mm thick armasound | 60 | Sqm | 0 | 0 | 0 | 0 | 0
Makes: Armacell/A Flex/ K Flex/Equivalent
4 | Supply Air Grill
| Supplying, fixing testing commissioning of supply air grill of powder coated aluminium with aluminium volume control dampers with anti smudge ring & removable core | 2.5 | Sqm | 0 | 0 | 0 | 0 | 0
Make: Mapro/ADS/System Air / Caryaire/Equivalent
5 | Return Air Grill
| Supplying, fixing testing commissioning of return air grill of powder coated aluminium without aluminium volume control dampers with anti smudge ring & removable core | 2.5 | Sqm | 0 | 0 | 0 | 0 | 0
Make: Mapro/ADS/System Air / Caryaire/Equivalent
| TOTAL SUB WORK 'B' |  |  | 0 | 0 | 0 | 0 | 0
SUB WORK 'C'- PLUMBING
1 | REFRIGERANT PIPING
Supply, Installation, testing and commissioning including vaccumiazation and Nitrogen testing of following nominal sizes of soft/hard drawn copper refrigerant piping for VRV/VRF system, complete with fittings, with suitable adjustable ring type hanger supports, jointing/brazing including accessories, insulated with XPLE Class-O tubular insulation/with Class-O closed cell elastometric nitrile rubber tubular sleeves sections of specified thickness as given below for Suction and Liquid lines, all accessories as per specifications etc. as required : Pipes shall pe laid in cable tray with closed wncloseure for safety from theft. Also all teh pipe shall be protected with external coating for extending the life of the pipes
1.1 | 15.86 mm dia (OD) (Soft drawn) with tube thickness 1.2 mm with 13 mm thick insulation | 30 | RM | 0 | 0 | 0 | 0 | 0
1.2 | 28.58 mm dia (OD) (Hard drawn) with tube thickness 1.2 mm with 19 mm thick insulation | 30 | RM | 0 | 0 | 0 | 0 | 0
NOTE:- (1) The Copper Piping & Piping Circuit should be with Minimum Number of joints, which shall be attained by : (i) Using One End Expanded Tubes (ii) Bending the tubes instead of using elbow joints wherever 90 degree bending is required. (2) Piping should be routed at site in such a manner, that brazed joints in the refrigeration piping are kept to a minimum. (3) The makes of tube fittings shall be same as that of tubes. (4) The thickness of fittings used shall be same as that of the pipe.
Makes of Copper Pipe: Mandev/Rajco/Maxflow/Equivalent
Makes of XLPE Insulation: Trocellen/CANI/Armacell / K Flex/Equivalent
2 | PVC Drain Piping
Supply, Installation, testing and commissioning of PVC piping complete with fittings, supports accessories in surface/recess as per specifications & site requirments including with duly insulated with 6 mm thick sleeve of nitrle rubber having K value 0.033 W/MK at 10 deg. C mean temp. and minimum density of 25 Kg/Cum. Insulation on drain pipe
2.1 | 25 mm Dia | 10 | m | 0 | 0 | 0 | 0 | 0
2.2 | 32 mm dia | 35 | m | 0 | 0 | 0 | 0 | 0
Makes: AKG/Supreme/Astral/Equivalent
| TOTAL SUB WORK 'C' |  |  | 0 | 0 | 0 | 0 | 0
D | SUB WORK 'D'- ELECTRIC WORKS
1 | Power Cabling
Supply and laying of the following 1100 volt grade armoured XLPE insulated and PVC sheathed aluminium conductor cable in trench / cable tray /clamped to wall with suitable clamps saddles & fixing bolts/including testing & commissioning complete as required. The costs shall include crimping tinned heavy duty alluminium lugs, compression glands requisite materials for all cables and to provide with 1D gap & shall be properly clamped with cable clamps & ties. Identification tags shall be provided for all cables including cable end termination.
1.1 | 4 core 10 Sq mm | 50 | RM | 0 | 0 | 0 | 0 | 0
Makes: Polycab/Havells/Finolex /Equivalent
2 | CONTROL CABLING
Supply, laying, testing and commissioning of PVC insulated and PVC sheathed, unarmoured, Copper Conductor of 1.1 KV grade on existing cable trays as per Standard specification including end termination as required.
2.1 | 6C x 1.5 Sq mm | 50 | RM | 0 | 0 | 0 | 0 | 0
Makes: Polycab/Havells/Finolex /Equivalent
3 | Electrical Cable Tray
Supply and installation of following size of perforated painted with powder coating G.I. cable trays with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with G.I. suspenders including bolts & nuts, painting suspenders etc as required.
3.1 | 150 mm width X 50 mm depth X 1.6 mm thickness | 30 | RM | 0 | 0 | 0 | 0 | 0
Makes: Legrand/MEM/ Schneider/Coblofil /Equivalent
4 | Earthing
| Providing and fixing 6 SWG dia G.I. wire on surface or in recess for loop earthing as required. | 40 | RM | 0 | 0 | 0 | 0 | 0
5 | Electrical Panel
| SITC of main electrical panel- 6 way TPN ( vertiacal ) consisting of MCCB- 125 AMP for main incomer and three outgoing MCB's of required power rating as per OEM design criteria including all cables for termination and accessories such as gland thimble etc to make system functional | 1 | no | 0 | 0 | 0 | 0 | 0
Makes: ABB/Seimens/CPRI APPROVED Equivalent
| TOTAL SUB WORK 'D' |  |  | 0 | 0 | 0 | 0 | 0
1 | SUB WORK 'A'-MACHINERY |  |  | 0 | 0 | 0 | 0 | 0
2 | SUB WORK 'B'- AIR DISTRIBUTION |  |  | 0 | 0 | 0 | 0 | 0
3 | SUB WORK 'C'- PLUMBING |  |  | 0 | 0 | 0 | 0 | 0
4 | SUB WORK 'D'- ELECTRIC WORKS |  |  | 0 | 0 | 0 | 0 | 0
Total in figures |  |  |  | 0 | 0 | 0 | 0 | 0
Quoted Rate in Words
| Controller of Administration |  |  |  | Seal & Signature of Contractor