## Sheet1
Item Wise BoQ
BoQ_Ver3.1 | Item Wise |  | INR and Other Currency
Tender Inviting Authority: Director, NIPGR, New Delhi
Name of Work:Supply, Installation, Testing & Commissioning of electrical facilities for VRV units at NIPGR Campus, New Delhi.
Contract No: NIPGR/Engg./6/6(4)/2025-26
Name of the Bidder/ Bidding Firm / Company :
PRICE SCHEDULE (This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevant columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only )
(This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevant columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only )
NUMBER # | TEXT # | NUMBER # | TEXT # | NUMBER # | NUMBER | NUMBER # | NUMBER # | NUMBER #
Sl. No. | Item Description | Quantity | Units | UNIT RATE In Figures To be entered by the Bidder in Rs. P | GST in Rs. P (Col. 5 x % of GST) | Total Unit Rate with GST (Col. 5+6) | TOTAL AMOUNT Without Taxes in Rs. P (Col. 3 x 5) | TOTAL AMOUNT With Taxes in Rs. P (Col. 3 x 7)
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9
1 | Supply, laying, testing & commissioning of 1100 volt grade armoured XLPE insulated, innersheath of PVC tape, and overall PVC sheathed aluminium conductor cable confirmimg to IS 7098 (part-1) of 2 runs of 3.5C x 120 sqmm size direct in ground, including excavation, sand cushioning, protective covering, refilling the trench as required as per CPWD specifications & instructions of Engineer in Charge. (The cable total length is 380 mtrs (2x190 mtrs), and trench length is 190 mtrs). | 190 | Rmt. | 0 | 0 | 0 | 0 | 0
2 | Supplying and making end termination with brass compression gland and aluminium lugs for cable of 3.5C x 120sqmm size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required & instructions of Engineer in Charge. | 4 | Each | 0 | 0 | 0 | 0 | 0
3 | Main Distribution Board
Design, manufacture, testing at works, supply, installation, testing, and commissioning of the following: A front-operated, front-access, cubicle-type panel fabricated from 2mm thick sheet steel, dust and vermin proof, double door construction, IP66 rated, complete with hinged and lockable doors, detachable top cover, internal interconnections by copper tapes/wires, painting, copper crimping lugs, brass glands, bonding to earth, and epoxy painting. The panel shall be suitable for operation at 415V, 3-phase, 4-wire, 50Hz system, complying with IS specifications and instructions of the Engineer-in-Charge (E.I.C.).
All live accessible parts shall be shrouded, and all equipment shall be finger-touch proof. The bus bar insulation shall be provided using heat-shrinkable sleeves. SMC/DMC busbar supports shall be used. A padlocking facility shall be provided. Necessary gaskets for doors, flexible earthing, and danger boards shall be provided. The gland plate shall be 3mm thick with knockouts.
INCOMING
1 No. 250A TP MCCB with 25kA service breaking capacity, adjustable trip settings, overcurrent protection, magnetic short-circuit release, and heavy-duty solid neutral link.
INDICATING PANEL The incoming feeder shall have the following indicating instruments: Digital Ammeter of required range with associated CTs. Digital Voltmeter. 3 Nos. Phase Indicating Lamps (each backed up with MCB). 2 Nos. ON/OFF indicating lamps for incomer feeder to indicate feeder status.
BUS BAR Electrolytic high-conductivity aluminium busbar for three phases and neutral. Busbar rated for 250A with a maximum current density of 1A per sqmm. Neutral busbar shall be of 100% capacity of the phase busbars.
OUTGOINGS
| 6 Nos. 63A, 4P MCBs, 10kA service breaking capacity, with overcurrent and magnetic short circuit protection, and heavy-duty solid neutral links. | 1 | Each | 0 | 0 | 0 | 0 | 0
4 | Providing and fixing 25 mm X 5 mm G.I. strip on surface or in recess and connections etc. as required & instructions of Engineer in Charge. | 20 | Rmt. | 0 | 0 | 0 | 0 | 0
Total in figures | [6 empty] | 0 | 0
Quoted Rate in Words
| Controller of Administration |  |  |  | Seal & Signature of Contractor